## Sheet1
Inputs |  |  | Table PEX Tube Sizes
Room air temperature (F) | 70 | Size | ID (") | OD (") | Thick (")
|  | 3/8" | 0.36 | 0.5 | 0.07
tube OD (") | 0.5 | 1/2" | 0.485 | 0.625 | 0.07
tube thickness (") | 0.07 | 5/8" | 0.574 | 0.75 | 0.088
tube wall conductivity (W/m-K) | 0.4 | 3/4" | 0.681 | 0.875 | 0.097
tube length (') | 150 | 1" | 0.875 | 1.125 | 0.125
Fluid Temperature entering tube (F) | 105
water or antifreeze flow (gpm) | 0.25
water or antifreeze sp heat (kJ/kg-K) | 4.2
water or antifreeze transfer coeff (W/m^2-K) | 200
Conductive plate width (") | 4
Floor or Ceiling Material thickness (") | 0.5
Floor or Ceiling conductivity (W/m-K) | 0.16
Outputs
Ut tube overall transfer coeff (W/m^2-K) | 105.8761
Uw wall overall transfer coeff (W/m^2-K | 5.2497
Utot combined transfer coeff (W/m^2-K) | 4.6609
Rtot (m^2-K/W) | 0.21455
Rtot (h-ft^2-F/Btu) | 1.2122
Effective Surface Area (conductive plate,ft^2) | 50
Effective Surface Area (conductive plate,m^2) | 4.6452
Tube outlet fluid temperature (F) | 94.9064
Floor/Ceiling surface temperature (F) | 85.3642
Heat Transfer per plate area (W/m^2) | 76.8212
Heat Transfer per plate area (Btu/h-ft^2) | 24.4694
Heat Transfer (W) | 356.8461
Heat Transfer (Btu/h) | 1223.4724
Tube
Conductive plate
Floor or Ceiling Material
Plate Width
Floor or Ceiling thickness
Floor or Ceiling Surface Temperature